## Detailed Measures
Victoria City Center
Sep 2025
Draft
No. | Measure |  | Category | Base Cost (€) | S1 inc | S2 inc | S3 inc | S4 inc | S5 inc | S1 (€) | S2 (€) | S3 (€) | S4 (€) | S5 (€)
1 | Façade sealing + blower door testing | Whole-building test + targeted smoke/infrared thermal scans scans; seal façade joints, door gaskets, shaft penetrations. | Energy Efficiency | 56760 | 1 | 1 | 1 | 1 | 1 | 56760 | 56760 | 56760 | 56760 | 56760 | P x H | 110 x 43 | 4730 | Provision
2 | Thermal imaging + patch insulation | Night infrared thermal survey of façades, roof, and ground-floor slab; punch-list of defects; patch insulation at parapets, slab edges, and window perimeters. | Energy Efficiency | 42570 | 1 | 1 | 1 | 1 | 1 | 42570 | 42570 | 42570 | 42570 | 42570 |  |  |  | Provision
3 | Air-source heat pumps (2×670 kW) | For offices: 2×670 kW air-to-water units (modular) on the roof/courtyard; EER=3.5,COP 3, | Electrification | 505000 | 1 | 0 | 0 | 0 | 1 | 505000 | 0 | 0 | 0 | 505000 | 2 unități670 kW-€240,000 – €360,000, Instalare profesională: €20,000 – €50,000; Structură de susținere pe acoperiș; Sisteme de control și integrare BMS; + 10,000Eur Crane
4 | Server room 100 kW 4-pipe HP | Replace the 100 kW server chiller with same capacity 4-pipe HP + dry cooler/economizer, EER = 3.5, COP = 3 | Electrification | 100000 | 1 | 1 | 0 | 0 | 1 | 100000 | 100000 | 0 | 0 | 100000 | ComponentăPreț estimativ (€)Chiller 100 kW (4-pipe HP)€45,000 – €70,000Dry cooler / economizer€10,000 – €20,000Controlere & automatizare€5,000 – €10,000Instalare & punere în funcțiune€10,000 – €20,000 Total estimativ €70,000 – €120,000, + 5,000 Eur Crane
5 | Condensing boilers (2×300 kW) | Modular cascade 2×300 kW condensing boilers (final size after calculating peak heat with optimizations) | Energy Efficiency | 87500 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 87500 | 87500 | 2 unități (€)Cazan în condensare 300 kW€25,000 – €40,000€50,000 – €80,000Kit de cascadă + accesorii€5,000 – €10,000€5,000 – €10,000Instalare și punere în funcțiune€10,000 – €20,000€10,000 – €20,000 Total estimativ — €65,000 – €110,000
6 | AHU replacement (1–2 units) | Retrofit rotary or counter-flow plate HR achieving η≥80%; if existing casings limit, replace AHUs serving offices, assume 1 AHU with the same airflow capacity as the previous (39000m3) | Energy Efficiency | 81500 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 81500 | 0 | 81500 | Recuperator rotativ / contracurent HR€8,000 – €15,000AHU nouă completă (39.000 m³/h)€35,000 – €60,000Automatizare & control BMS€5,000 – €10,000Demontare & instalare AHU€10,000 – €20,000 Total estimativ €58,000 – €105,000; Retrofit approx.€ 30,000
7 | VAV boxes + controls | 1 VAV box per floor → 10 boxes total; add duct static-pressure sensors and controller. | Energy Efficiency | 12400 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 12400 | 0 | 0 | 10 unități (€)VAV box (standard, cu reheat)€600 – €1,200€6,000 – €12,000Senzor presiune statică (duct) €80 – €150, €800 – €1,500Controler VAV (digital/pneumatic)€150 – €300 €1,500 – €3,000 Total estimativ — €8,300 – €16,500
8 | CO₂ sensors (30–40 pcs) | 1 CO₂ sensor per zone or per ~250 m² → 30–40 sensors; integrate into OA/VAV control. | Energy Efficiency | 18550 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 18550 | 0 | 0 | 30–40 unități (€)Senzor CO₂ (cu Modbus/BACnet)€120 – €250 per item, €3,600 – €10,000 cumulated; Controlere VAV compatibile €150 – €300 per item, €4,500 – €12,000 cumulated; Integrare în sistem OA/VAV€2,000 – €5,000 item, €2,000 – €5,000 cumutated; Total estimativ — €10,100 – €27,000
9 | Window sensors (estimated 100 pcs) | 1 magnetic contact per operable window; interlock FCU/AHU VAV close. | Energy Efficiency | 14350 | 1 | 0 | 1 | 0 | 1 | 14350 | 0 | 14350 | 0 | 14350 | 100 unități (€)Contact magnetic (cu fir, tip NC/NO)€5 – €15 item , €500 – €1,500 cumulated; Cablu, accesorii, conectori€2 – €5 item, €200 – €500 cumulated; Control logic / interfață BMS€50 – €150 item, €5,000 – €15,000 cumulated; Manoperă montaj și testare sistem€20 – €40 item, €2,000 – €4,000 cumulated; Total estimativ cu montaj — €7,700 – €21,000
10 | LED retrofit (estimated for 5,000m2) | Remaining fluorescent lamps→ LED; target ≤7–8 W/m² office light density | Energy Efficiency | 55000 | 1 | 1 | 1 | 1 | 1 | 55000 | 55000 | 55000 | 55000 | 55000 | Corp LED (40W, 4000K, 120 lm/W)€25 – €45€21,875 – €45,000Demontare fluorescent + montaj€10 – €20€8,750 – €20,000Controlere / senzori (opțional)€5 – €10€4,375 – €10,000 Total estimativ - €35,000 – €75,000
11 | Daylight + motion sensors | 1 daylight sensor per façade zone(4total), 20–30 sensors in corridors, 20 sensors for toilets | Energy Efficiency | 8960 | 1 | 0 | 1 | 0 | 1 | 8960 | 0 | 8960 | 0 | 8960 | Senzori daylight (fațadă)€80 – €150 item, €320 – €600 cumulated; Senzori coridor (microwave/PIR)€40 – €80item, €800 – €2,400 cumulated; Senzori toaletă (PIR/IP65)€40 – €70, €800 – €1,400; Controlere / interfață BMS€50 – €150, €2,000 – €4,000; Manoperă montaj și testare€30 – €50/senzor, €2,100 – €3,500; Total estimat - €6,020 – €11,900
12 | Advanced BMS upgrade | Upgrade BMS server + analytics pack; connect all AHUs, pumps, chillers/HPs, boilers, meters. | Energy Efficiency | 105500 | 1 | 1 | 1 | 1 | 1 | 105500 | 105500 | 105500 | 105500 | 105500 | Server BMS nou (hardware + software)€15,000 – €30,000Pachet de analiză energetică (analytics)€10,000 – €25,000Controlere și interfețe pentru echipamente€20,000 – €40,000Integrare contoare (energie, apă, gaz)€5,000 – €10,000Licențe software + cloud (dacă e cazul)€3,000 – €8,000/anManoperă, programare, testare€15,000 – €30,000 Total estimativ €68,000 – €143,000
13 | Standard BMS upgrade |  | Energy Efficiency | 60000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Provisional Sum
14 | Sub-metering | Separate electric meters on: AHU fan, CHW/HHW pump groups, tenant heating and cooling, lighting; Gas sub meter for boilers vs. tenants | Energy Efficiency | 22550 | 1 | 1 | 1 | 1 | 1 | 22550 | 22550 | 22550 | 22550 | 22550 | Contor electric trifazat (AHU fan)4€250 – €500, €1,000 – €2,000; Contoare pompe CHW/HHW (grupuri separate)6–8€250 – €500, €1,500 – €4,000; Contoare chiriași (încălzire/răcire)10–15€, 300 – €600, €3,000 – €9,000; Contoare iluminat zonal 8–12€, 200 – €400, €1,600 – €4,800; Subcontoare gaz (cazane vs. chiriași)2–3€, 400 – €800, €800 – €2,400; Panou de integrare + cablare + montaj——€5,000 – €10,000; Total estimativ - €12,900 – €32,200
15 | Shading (700 m² façade) | Motorized venetian blinds or fixed fins on W/S façades (700m2) | Energy Efficiency | 227500 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 227500 | 0 | Jaluzele venețiene motorizate €250 – €400, €175,000 – €280,000; Lamele fixe (fins) €150 – €250, €105,000 – €175,00;
16 | Roof insulation +10–12 cm PIR | Add +10–12 cm PIR (λ≈0.022) to reach U≤0.18 W/m²K; roof area ~1500 m² | Energy Efficiency | 82500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 m² (€)Panouri PIR (10–12 cm grosime)€25 – €40, €37,500 – €60,000; Adeziv, fixare mecanică, etanșare€5 – €10, €7,500 – €15,000; Manoperă montaj profesional€10 – €20, €15,000 – €30,000; Total estimativ - €60,000 – €105,000
17 | Window films (1,000 m² glass) | Apply to W/S/E façades (estimate 1000 m² of glass in total); g-value <0.45, visible transmittance ≥50%. | Energy Efficiency | 90000 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 90000 | 0 | 1000 m² (€) Folie solară profesională €60 – €120, €60,000 – €120,000;
18 | Rooftop PV (120 kWp) | Usable roof 500 m² → 120 kWp (240 panels); string inverter(s) with export-limit if needed | Photovoltaic | 96000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Provisional Sum (without metallic supporting structures if required)
19 | Solar thermal DHW (25 m²) | Usable roof 500 m² → 120 kWp (240 panels); string inverter(s) with export-limit if needed | Photovoltaic | 16500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Provisional Sum (without metallic supporting structures if required)
20 | Install VSD (variable speed drive) on AHU fans. | Fit VSDs sized to each fan motor; add static-pressure reset logic. | Energy Efficiency | 18650 | 1 | 0 | 1 | 0 | 1 | 18650 | 0 | 18650 | 0 | 18650 | VSD (pentru motoare 5–15 kW)6–10, €600 – €1,200, €3,600 – €12,000; Senzor presiune statică (conductă)6–10, €80 – €150, €480 – €1,500; Controler logică reset presiune (DDC/BMS)1 sistem €2,000 – €5,000, €2,000 – €5,000; Manoperă + cablare + integrare——€4,000 – €8,000; Total estimativ - €10,080 – €26,500
21 | Plant optimization software for load sequencing and efficiency. | Software module +input/output to all major pumps/fans/chillers/boilers; include fault-rules (valve leakage, low temperature difference ΔT, high pressure difference ΔP). | Energy Efficiency | 56000 | 1 | 0 | 1 | 1 | 1 | 56000 | 0 | 56000 | 56000 | 56000 | Software modul BMS + licență fault analytics €10,000 – €25,000; Controlere I/O pentru pompe, ventilatoare etc.€8,000 – €15,000; Senzori suplimentari (ΔT, ΔP, poziție valve) €5,000 – €10,000; Programare reguli de detecție defecțiuni€3,000 – €6,000; Integrare în BMS existent / cloud€5,000 – €10,000; Manoperă, testare, punere în funcțiune€5,000 – €10,000; Total estimativ complet €36,000 – €76,000
22 | Variable-speed pumps in heating and cooling circuits with demand-based control | VSDs on primary/secondary HHW & CHW pumps; add ΔP sensors on risers | Energy Efficiency | 19250 | 1 | 1 | 1 | 1 | 1 | 19250 | 19250 | 19250 | 19250 | 19250 | VSD-uri pentru pompe HHW/CHW (5–15 kW)6–10, €600 – €1,200, €3,600 – €12,000; Senzori ΔP pe coloane (Modbus/BACnet)6–10, €150 – €300, €900 – €3,000; Controlere / integrare în BMS1 sistem €2,000 – €5,000, €2,000 – €5,000; Manoperă, cablare, testare——€4,000 – €8,000; Total estimativ - €10,500 – €28,000
23 | Integrate boilers with heat pumps for hybrid operation (heat pump for base load, boilers for peaks). | Air-to-water heat pumps base-load + condensing boilers for peaks (see #3 for HP type). Hydraulic separator + smart bivalence control | Energy Efficiency | 182000 | 1 | 1 | 0 | 0 | 1 | 182000 | 182000 | 0 | 0 | 182000 | Pompe de căldură aer-apă (base load) €20,000 – €50,000/unit €40,000 – €100,000 (2 unități); Cazane în condensare (peak load) €25,000 – €40,000/unit, €50,000 – €80,000 (2 unități); Separator hidraulic + accesorii €3,000 – €6,000, €3,000 – €6,000; Controler bivalent inteligent (BMS) €5,000 – €10,000, €5,000 – €10,000; Senzori, vane, cablare, integrare —€10,000 – €20,000; Manoperă, testare, punere în funcțiune —€15,000 – €25,000; Total estimativ - €123,000 – €241,000;
24 | Add free cooling / economizer cycles when climate permits. | Enable integrated free cooling on new chiller/HP(see #4 for HP type). | Energy Efficiency | 40500 | 1 | 0 | 0 | 1 | 1 | 40500 | 0 | 0 | 40500 | 40500 | Modul de freecooling integrat (hardware)€15,000 – €30,000; Automatizare și control logic (BMS) €5,000 – €10,000S; Senzori suplimentari (temperatură, debit) €2,000 – €4,000; Manoperă, cablare, testare €5,000 – €10,000; Total estimativ complet €27,000 – €54,000;
25 | Occupancy sensors in offices, meeting rooms (estimate 70-115). | 1 sensor per small room, 2–3 per large open-plan | Energy Efficiency | 18550 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 18550 | 0 | 18550 | Senzor PIR / ultrasonic (standard) €40 – €120, €2,800 – €13,800; Controler / interfață BMS €50 – €150, €3,500 – €8,000; Cablare + montaj + testare€30 – €60 / senzor, €2,100 – €6,900; Total estimativ - €8,400 – €28,700;
26 | BMS-integrated lighting control for scheduling and dimming. | in BMS: Time-schedules + scenes per floor; tie to access logs for real occupancy. | Energy Efficiency | 100000 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100000 | Software BMS lighting module (scheduling/scenes) €10,000 – €20,000; Controlere DALI/KNX per etaj €5,000 – €10,000 / etaj; Senzori de lumină + prezență (pentru scenarii)€40 – €120 / senzorInterfață cu sistem de acces (API/licență), €3,000 – €6,000; Programare scenarii + logica ocupare €5,000 – €10,000; Manoperă, cablare, testare €10,000 – €20,000; Total estimativ - €60,000 – €140,000;
27 | Task lighting to reduce overall ambient lighting levels. | Provide desk lamps for tenants; reduce LED ambient set point from 500→300–350 lx. | Energy Efficiency | 65000 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 65000 | 65000 | 0 | Lămpi de birou (1 per stație de lucru)~600–1000, €25 – €69, €15,000 – €69,000; Ajustare iluminat ambiental LED (dimming)——€5,000 – €10,000; Reconfigurare BMS / control iluminat——€10,000 – €20,000; Total estimativ - €30,000 – €99,000;
28 | Dynamic set point temperature control based on occupancy, outdoor temperature, and time of day. | Weather-based setback: night/weekend 15–16 °C on vacant floors; HHW curve; CHW reset at low load. Ex. AI assisted software Honeywell Forge | Energy Efficiency | 101500 | 1 | 0 | 1 | 0 | 1 | 101500 | 0 | 101500 | 0 | 101500 | Licență software AI-assisted (Honeywell Forge etc.)€20,000 – €40,000; Controlere și interfețe I/O pentru echipamente€15,000 – €30,000; Senzori suplimentari (ocupare, temperatură, ΔT, ΔP) €8,000 – €15,000; Integrare cu BMS existent / cloud €10,000 – €20,000; Programare logică dinamică + curbe HHW/CHW€5,000 – €10,000; Manoperă, testare, punere în funcțiune€10,000 – €20,000; Total - €68,000 – €135,000;
29 | Automated fault detection in BMS to catch equipment inefficiencies early. | BMS capability for library for filter ΔP, valve leakage, coil fouling, sensor drift, HR bypass; needs ~2–4 weeks of trend to tune | Energy Efficiency | 79000 | 1 | 1 | 1 | 1 | 1 | 79000 | 79000 | 79000 | 79000 | 79000 | Licență software FDD (ex. Honeywell Forge, Facilio, Schneider EcoStruxure) €20,000 – €40,000; Controlere și interfețe I/O suplimentare €10,000 – €20,000; Senzori suplimentari (ΔP, temperatură, debit etc.) €5,000 – €10,000; Programare regulilor FDD + tuning algoritmi €8,000 – €15,000; Integrare în BMS existent €5,000 – €10,000; Manoperă, testare, punere în funcțiune €5,000 – €10,000; Total estimativ - €53,000 – €105,000;
30 | Zone-level climate control for different office areas to match occupancy patterns. | BMS software to split building by floor/wing, VAV/FCU groups per zone, independent schedules and set points. Ex. AI assisted software Honeywell Forge | Energy Efficiency | 112500 | 1 | 1 | 1 | 1 | 1 | 112500 | 112500 | 112500 | 112500 | 112500 | Licență software AI-assisted (Honeywell Forge, Siemens Desigo, Johnson CPO) €25,000 – €50,000; Controlere zonale (VAV/FCU) + interfețe BMS, €20,000 – €40,000; Senzori de temperatură, CO₂, prezență €10,000 – €20,000; Programare logică zonală + scenarii per etaj/wing €5,000 – €10,000; Integrare cu sistem de acces / ocupare reală €5,000 – €10,000; Manoperă, cablare, testare €10,000 – €20,000; Total estimativ complet €75,000 – €150,000;
31 | Integration with weather forecasts for proactive heating/cooling adjustments. | BMS plug-in using 24–48 h forecast for pre-heat/pre-cool and proactive economizer. Ex. AI assisted software Honeywell Forge | Energy Efficiency | 75000 | 1 | 0 | 1 | 0 | 1 | 75000 | 0 | 75000 | 0 | 75000 | Licență software AI-assisted (ex. Honeywell Forge, Siemens Desigo CC, Johnson CPO ) €20,000 – €40,000; Modul de integrare meteo + API forecast €5,000 – €10,000; Controlere suplimentare / interfețe I/O €10,000 – €20,000; Programare logică pre-heat/pre-cool + economiser €5,000 – €10,000; Senzori suplimentari (temperatură, CO₂, debit, poziție vane) €5,000 – €10,000; Manoperă, testare, punere în funcțiune €5,000 – €10,000; Total estimativ - €50,000 – €100,000;
32 | Load shedding strategies in BMS (e.g., dimming lights, reducing non-critical HVAC loads during peak hours). | BMS scenes: dim lights −20%, relax set points ±1–2 C, delay non-critical pumps during peaks. | Energy Efficiency | 56000 | 1 | 0 | 1 | 0 | 1 | 56000 | 0 | 56000 | 0 | 56000 | Modul software BMS pentru scene și shedding €10,000 – €25,000; Controlere suplimentare pentru pompe/lumină €8,000 – €15,000; Interfață cu sistemul de iluminat (DALI/KNX) €5,000 – €10,000; Programare logică de scenarii și priorități €5,000 – €10,000; Integrare cu senzorii de sarcină / peak alerts €3,000 – €6,000; Manoperă, testare, punere în funcțiune €5,000 – €10,000; Total estimativ complet €36,000 – €76,00;
33 | Predictive maintenance based on equipment runtime and performance trends. | Use equipment runtime, starts, pressure difference (ΔP), and temperature difference (ΔT) to auto-create maintenance work orders; integrate with BMS | Energy Efficiency | 78000 | 1 | 0 | 1 | 0 | 1 | 78000 | 0 | 78000 | 0 | 78000 | Licență software FDD + modul de mentenanță predictivă €20,000 – €40,000; Controlere și interfețe I/O suplimentare €10,000 – €20,000; Senzori suplimentari (ΔP, ΔT, runtime, stare echipament) €5,000 – €10,000; Integrare cu BMS și sistem de ticketing/CMMS €5,000 – €10,000; Programare logică de declanșare automată €5,000 – €10,000; Manoperă, testare, punere în funcțiune €5,000 – €10,000; Total estimativ - €50,000 – €100,000;
34 | TOTAL I |  |  |  | S1 (€): 1729090; S2 (€): 775130; S3 (€): 1097590; S4 (€): 1059630; S5 (€): 2016640
35 | Profit + Indirect (20%) |  |  |  | S1 (€): 345818; S2 (€): 155026; S3 (€): 219518; S4 (€): 211926; S5 (€): 403328
36 | Soft Costs (10%) |  |  |  | S1 (€): 172909; S2 (€): 77513; S3 (€): 109759; S4 (€): 105963; S5 (€): 201664
37 | Contingency (15%) |  |  |  | S1 (€): 259363.5; S2 (€): 116269.5; S3 (€): 164638.5; S4 (€): 158944.5; S5 (€): 302496
38 | GRAND TOTAL |  |  |  | S1 (€): 2507180.5; S2 (€): 1123938.5; S3 (€): 1591505.5; S4 (€): 1536463.5; S5 (€): 2924128

## Cost Parameters
Parameter | Value | Notes
GLA (m²) | 11599 | Used for €/kWh calc
Perimeter(m) | 110 | Used for façade area
Height(m) | 43 | Used for façade area
Profit + Indirect (%) | 0.2 | Applied to Hard Costs
Soft Costs (%) | 0.1 | Applied to Hard Costs
Contingency (%) | 0.15 | Applied to Hard Costs

## Scenario Totals
Scenario No. | S1 | S2 | S3 | S4 | S5
Hard Costs | 1729090 | 775130 | 1097590 | 1059630 | 2016640
Profit + Indirect | 345818 | 155026 | 219518 | 211926 | 403328
Soft Costs | 172909 | 77513 | 109759 | 105963 | 201664
Contingency | 259363.5 | 116269.5 | 164638.5 | 158944.5 | 302496
Grand Total | 2507180.5 | 1123938.5 | 1591505.5 | 1536463.5 | 2924128

## Payback Duration
Nr. Crt. | Scenario | yearly gas and electricity consumption [kWh] | yearly energy savings compared to current consumption[kWh] | energy savings cost/yr [EUR] | Scenario cost [EUR] | payback duration [yr] | ROI [%]
1 | Scenario 1 | 866553.71 | 970993.21 | 223328.4383 | 2507180.5 | 11.2264 | 8.908%
2 | Scenario 2 | 1277706.11 | 559840.81 | 128763.3863 | 1123938.5 | 8.7287 | 11.46%
3 | Scenario 3 | 1107696.54 | 729850.38 | 167865.5874 | 1591505.5 | 9.4808 | 10.55%
4 | Scenario 4 | 1308496.1 | 529050.82 | 121681.6886 | 1536463.5 | 12.6269 | 7.92%
5 | Scenario 5 | 772379.57 | 1065167.35 | 244988.4905 | 2924128 | 11.9358 | 8.378%
6 | Baseline(actual) | 1837546.92 | 0 | 0
Average Price/kWh actual - Electricity 0.3 EUR - Gas 0.08
Average price electricity and gas for project: 2/3 x 0.3 + 1/3 x 0.08 = 0.23 EUR/kWh |  |  |  |  | 0.23

## Scenario 2 Phasing
Victoria City Center
Sep 2025
Draft
Scenario 2 Phasing
No. | Measure |  | Category | Base Cost (€) | S2 inc | S2 (€) |  | Phase 1 | Phase 2 | Phase 3
1 | Façade sealing + blower door testing | Whole-building test + targeted smoke/infrared thermal scans scans; seal façade joints, door gaskets, shaft penetrations. | Energy Efficiency | 56760 | 1 | 56760 | 4730 | Undertake initial Cladding Assesement - 3 months
2 | Thermal imaging + patch insulation | Night infrared thermal survey of façades, roof, and ground-floor slab; punch-list of defects; patch insulation at parapets, slab edges, and window perimeters. | Energy Efficiency | 42570 | 1 | 42570
4 | Server room 100 kW 4-pipe HP | Replace the 100 kW server chiller with same capacity 4-pipe HP + dry cooler/economizer, EER = 3.5, COP = 3 | Electrification | 100000 | 1 | 100000 |  |  |  | Replace when chiller is close to expected lifespan. - 6 months
10 | LED retrofit | Remaining fluorescent lamps→ LED; target ≤7–8 W/m² office light density | Energy Efficiency | 55000 | 1 | 55000 |  | Ongoing as tenant space becomes available for such actions
12 | Advanced BMS upgrade | Upgrade BMS server + analytics pack; connect all AHUs, pumps, chillers/HPs, boilers, meters. | Energy Efficiency | 105500 | 1 | 105500 |  |  |  | Implement 1 year
14 | Sub-metering | Separate electric meters on: AHU fan, CHW/HHW pump groups, tenant heating and cooling, lighting; Gas sub meter for boilers vs. tenants | Energy Efficiency | 22550 | 1 | 22550 |  |  | Implement - 3 months
22 | Variable-speed pumps in heating and cooling circuits with demand-based control | VSDs on primary/secondary HHW & CHW pumps; add ΔP sensors on risers | Energy Efficiency | 19250 | 1 | 19250 |  |  |  | Linked to BMS
23 | Integrate boilers with heat pumps for hybrid operation (heat pump for base load, boilers for peaks). | Air-to-water heat pumps base-load + condensing boilers for peaks (see #3 for HP type). Hydraulic separator + smart bivalence control | Energy Efficiency | 182000 | 1 | 182000 |  |  |  | Replace / Integrate as equipment lifespan expires - 6 to 9 months
29 | Automated fault detection in BMS to catch equipment inefficiencies early. | BMS capability for library for filter ΔP, valve leakage, coil fouling, sensor drift, HR bypass; needs ~2–4 weeks of trend to tune | Energy Efficiency | 79000 | 1 | 79000 |  |  |  | Linked to BMS
30 | Zone-level climate control for different office areas to match occupancy patterns. | BMS software to split building by floor/wing, VAV/FCU groups per zone, independent schedules and set points. Ex. AI assisted software Honeywell Forge | Energy Efficiency | 112500 | 1 | 112500 |  |  |  | Linked to BMS
34 | TOTAL I |  |  |  |  | 775130
35 | Profit + Indirect (20%) |  |  |  |  | 155026
36 | Soft Costs (10%) |  |  |  |  | 77513
37 | Contingency (15%) |  |  |  |  | 116269.5
38 | GRAND TOTAL |  |  |  |  | 1123938.5